## Slide 1
Fiber Optic Measurement Technique
Piotr Turowicz
Poznan Supercomputing and Networking Center
piotrek@man.poznan.pl
Training Session
Kiev
9-10 October 2006
.
http://www.porta-optica.org

## Slide 2: Testing and Measuring
Testing a cabling infrastructure is important to:
  Identify faults or help in trouble shooting
  Determine the system quality and its compliance to Standard
  Allow recording performance of the cabling at time zero
Testing FO cabling is an indirect process
  Measurement of link length and loss
  Compare with values calculated at design time
  (workmanship quality)
  Compare with Standard defined values (link functionality)

## Slide 3: Power budget
Calculation of theoretical insertion loss at 850nm
Components
Fiber 50/125 0.25 km at 3.5dB (1.0dB) 0.875
Connector 3 pcs. at 0.5dB 1.5
Splice 1 pcs. at 0.1dB 0.1___
Total attenuation 2.475
Connection
Splice
Connection
Connection
70 m
150 m
30 m
PMD
PMD
Notes: The core is a thin filament made of glass or plastic, measured in micra (1 mm = 0,000001m), where the light passes through. The larger the diameter of the core, the more light it can conduct.
Cladding is around the core. Since it has a refraction index lower than the core, it prevents the light from being refracted, hence allowing the light to reach the reception device.
Jacket is around the cladding and provides physical and environmental protection for the fiber.

## Slide 4: FO field testers (measuring tools)
LIGHT tracer
– red light source and launching fiber
Power meter
– measuring tools for light power loss
OTDR
– graphical display of channel/link losses, location, behavior

## Slide 5: Attenuation measurement principles
OTDR
Backscatter measuring (OTDR)
Power measuring
Receiver
Transmitter
Receiver
Plug
Transmitter
Plug
OTDR
Plug
Plug

## Slide 6: Power meter measurement
Some basic rules
Light source
Laser only for singlemode fiber. LED for multi- and singlemode fibers.
PC to PC and APC to APC connectors on test equipment.
Do not disconnect launch cord after reference.
„heat up“ the source before using (10 min.)
Power Meter
Detector is very large and is not measured
Mode filter
For reliable measurements the use of a mode filter on the launch cord is essential.
Cleaning
Each connector should be cleaned before testing/application.

## Slide 7: Power measurement : level setting
1. Reference measuring
Transmitter
Test cable 1
Adjust:
attenuation = 0 dB
Receiver
Test cable 2

## Slide 8: Power measurement : link evaluation
Transmitter
2. Measuring the system’s attenuation
Receiver
FO System
Total attenuation [dB]

## Slide 9: Error reduction : the Mandrel wrap principle
50 m mandrel  18 mm for 3 mm jumpers
62.5 m mandrel  20 mm for 3 mm jumpers
9 m N.A.
Test jumper length 1 m to 5 m
Mandrel
launch cord
5 wraps
This “mode filter” causes high bend loss in loosely coupled modes and low loss in tightly coupled modes. Thus the mandrel removes all loosely coupled modes generated by an overfilled launch in a short (cords) link used during the reference setting

## Slide 10: Optical Time Domain Reflectometer (OTDR) block diagram
t
Measuring
delay
Receiver
Evaluation
Impuls
generator
Light
source
Beam
splitter
optical signals
electric signals
FO

## Slide 11: OTDR measuring : principle of operation
OTDR
The reflected light pulse is detected by the OTDR.
The light pulse is partly reflected by an interfering effect.
OTDR
A light pulse propagates in an optical waveguide.
OTDR

## Slide 12: Event dead zone in an OTD

## Slide 13: Attenuation dead zone in an OTDR

## Slide 14: Measuring with OTDR
1) launching fiber 2) launching fiber
200 m - 500 m for MM 200 m – 500 m for MM
500 m - 1’000 m for SM 500 m - 1’000 m for SM
FO system under test
1)
2)
Testing set up

## Slide 15
Errors detected by OTDR
Connection or mech./fusion splice
Fiber
Microbending
air gap
lateral off-set
different type of fiber
contamination
Fiber
Macrobending

## Slide 16: Optical Time Domain Reflectometer
Relative power
Distance

## Slide 17: An example of an OTDR waveform

## Slide 18: Dynamic ratio in an OTDR

## Slide 19: Other FO measueremnts
Chromatic Dispersion.
Polarisation Mode Dispersion
Only for Singlemode application Channel length > 2 km

## Slide 20: EXFO Equipement
Notes: The core is a thin filament made of glass or plastic, measured in micra (1 mm = 0,000001m), where the light passes through. The larger the diameter of the core, the more light it can conduct.
Cladding is around the core. Since it has a refraction index lower than the core, it prevents the light from being refracted, hence allowing the light to reach the reception device.
Jacket is around the cladding and provides physical and environmental protection for the fiber.

## Slide 21
EXFO Equipement
Broadband source (C+L) for CD/PMD
Videomicroscope

## Slide 22: CD tool

## Slide 23: CD result
http://www.porta-optica.org
Notes: MM fibers are typically used for small distances (a few kms) whereas SM fibers for long distance.
SM fibers can carry a few Tbps by deploying DWDM technology in comparison to MM fibers that are typically used for providing access to clients (order of Gbps)

## Slide 24: References
http://www.porta-optica.org
Reichle & De-Massari
Notes: MM fibers are typically used for small distances (a few kms) whereas SM fibers for long distance.
SM fibers can carry a few Tbps by deploying DWDM technology in comparison to MM fibers that are typically used for providing access to clients (order of Gbps)